# 4. Results & Discussion: BESS Impact on Feeder Voltage

# 4.1  Bus 675 Phase-A Voltage Profile Analysis

To evaluate the effectiveness of the integrated 350 kW / 1400 kWh Battery Energy Storage System (BESS) paired with solar PV, a 24-hour daily load flow analysis was performed on the IEEE 13-bus distribution feeder. Table 4.1 details the Phase-A voltage (V₁) at Bus 675 across the 24-hour dispatch cycle, comparing baseline feeder voltages against the BESS-supported grid state.

Table 4.1: 24-Hour Phase-A Voltage Comparison at Bus 675

| Hour | Before (V) | After (V) | ΔV Improvement (V) | % Improvement | BESS Operational State |
| --- | --- | --- | --- | --- | --- |
| 1 | 2366.73 | 2398.46 | +31.73 | +1.34% | Off-Peak Charging |
| 2 | 2381.83 | 2397.62 | +15.79 | +0.66% | Off-Peak Charging |
| 3 | 2396.70 | 2412.54 | +15.84 | +0.66% | Off-Peak Charging |
| 4 | 2411.38 | 2411.40 | +0.02 | +0.00% | Off-Peak Charging |
| 5 | 2410.32 | 2410.32 | 0.00 | 0.00% | Off-Peak Charging |
| 6 | 2395.79 | 2398.17 | +2.38 | +0.10% | Transition / Solar Ramp |
| 7 | 2366.74 | 2366.74 | 0.00 | 0.00% | Idling / PV Generation |
| 8 | 2352.20 | 2352.21 | +0.01 | +0.00% | Idling / PV Generation |
| 9 | 2336.59 | 2353.22 | +16.63 | +0.71% | PV Generation |
| 10 | 2336.68 | 2348.67 | +11.99 | +0.51% | PV Generation |
| 11 | 2318.92 | 2338.36 | +19.44 | +0.84% | Solar Peak / PV Support |
| 12 | 2317.46 | 2341.33 | +23.87 | +1.03% | Solar Peak / PV Support |
| 13 | 2299.35 | 2337.77 | +38.42 | +1.67% | Solar Peak / PV Support |
| 14 | 2280.19 | 2316.28 | +36.09 | +1.58% | Solar Peak / PV Support |
| 15 | 2299.65 | 2328.81 | +29.16 | +1.27% | Solar Taper / PV Support |
| 16 | 2318.65 | 2334.52 | +15.87 | +0.68% | Solar Taper |
| 17 | 2336.04 | 2357.52 | +21.48 | +0.92% | Discharge Start |
| 18 | 2299.73 | 2328.92 | +29.19 | +1.27% | Peak Evening Discharge |
| 19 | 2250.18 | 2303.02 | +52.84 | +2.35% | Maximum Peak Discharge |
| 20 | 2209.50 | 2209.50 | 0.00 | 0.00% | Idling / Standby |
| 21 | 2236.37 | 2236.37 | 0.00 | 0.00% | Idling / Standby |
| 22 | 2299.97 | 2299.97 | 0.00 | 0.00% | Idling / Standby |
| 23 | 2353.12 | 2353.12 | 0.00 | 0.00% | Idling / Standby |
| 24 | 2384.42 | 2384.42 | 0.00 | 0.00% | Idling / Standby |

# 4.2  Representative Voltage Improvement Calculations

The magnitude of voltage support provided by the BESS is calculated using the following governing relations:

Voltage Deviation:  ΔV  =  V_after  −  V_before

Percentage Improvement:  % Improvement  =  ( (V_after − V_before) / V_before ) × 100

## Peak Loading Hour (Hour 19)

During the maximum feeder demand period (Hour 19), the baseline Phase-A voltage drops to its lowest level before BESS intervention (V_before = 2250.18 V):

ΔV:  ΔV  =  2303.02 V  −  2250.18 V  =  52.84 V

% Improvement:  % Improvement  =  ( 52.84 V / 2250.18 V ) × 100  =  2.35 %

## Mid-Day Solar Transition (Hour 13)

At Hour 13, under high solar irradiance and moderate load demands (V_before = 2299.35 V):

ΔV:  ΔV  =  2337.77 V  −  2299.35 V  =  38.42 V

% Improvement:  % Improvement  =  ( 38.42 V / 2299.35 V ) × 100  =  1.67 %

# 4.3  Key Findings & System Interpretation

Direct Correlation with Dispatch Profile: The numerical results demonstrate a strong coupling between the BESS schedule (BESSShape) and the bus voltage. Voltage improvements occur exclusively when active power is being exchanged with the feeder.

Peak Sag Mitigation: The maximum voltage recovery occurs at Hour 19, yielding a 52.84 V (+2.35%) rise. This confirms that discharging BESS active power during peak loading hours effectively mitigates severe end-of-line voltage sags.

Mid-Day PV Integration Support: During Hours 9 through 16, combined PV generation and energy management maintain the line voltage comfortably above 2315 V, flattening the daily voltage profile.

Zero-Infiltration during Idle Hours: Between Hours 20 and 24, when the BESS multiplier is set to 0.0, the voltages before and after remain identical. This confirms that the simulation reflects accurate dispatch behavior without lingering mathematical offsets.

# 4.4  Thesis / Publication Summary Statement

"The integration of the 350 kW / 1400 kWh Battery Energy Storage System (BESS) co-located with solar PV significantly improved the voltage profile at the weak terminal node (Bus 675). During the peak loading interval at Hour 19, phase-A voltage was boosted from a baseline of 2250.18 V to 2303.02 V, representing a net voltage recovery of 52.84 V (2.35%). The observed voltage support directly aligns with the active power injection intervals of the programmed dispatch profile, confirming that localized storage effectively alleviates severe distribution-level voltage sags during critical peak periods."

IEEE 13-Bus Feeder | BESS: 350 kW / 1400 kWh | Simulation: 24-Hour Daily Load Flow | Phase-A Analysis at Bus 675